INTERFACE CONTROL DOCUMENT

for

LAUNCH PAD LIGHTNING WARNING SYSTEM

ELECTRIC FIELD  MILL TO

BASE STATION COMPUTER

COMMUNICATIONS

April 12, 1993

6 Electric Field Mill Data Record

The structure of the electric field mill data record and the elements comprising that structure are specified in this section.

6.1 Data Record Structure

The data record transmitted by the Electric Field Mill will consist of 114 bytes of mill operational status, potential gradient and raingauge data, and an error checking parameter.  The data record is summarized below with the "Byte No." indicating the number or position in the data record and the "Type" specifying the format of the information:

I = Two's complement 16 bit integer, Motorola byte order

UI = Unsigned 16 bit integer

BI = 16 bit binary pattern

C = Two's complement 8 bit integer

UC	=	Unsigned 8 bit integer

BC = 8 bit binary bit pattern

X = Not defined

Byte no.	Type	Function

1-2				BI		Synchronization Pattern

3					UC		Station Address

4					BC		Mode/Command Byte

5-11			-			Status Bytes 1-7

12				UC		Rain Gauge Tip Count

13-112		I/-		Potential Gradient Data or Extended Status Report

113-114		BI		CRC-16 Value

Depending on the operating mode of the mill, the data record transmitted will be of one of four types distinguished by the contents of the 100 byte Potential Gradient Data or Extended Status  Report:

Record Type			Contents

1. Normal				50 16-bit samples of potential gradient

2. Split				25 16-bit samples of potential gradient plus 25 16-bit samples of external signal

3. Calibration	50 16-bit samples of potential gradient (positive, negative, & zero imposed calibration fields)

4. Diagnostic		Extended status reporting (Self-Test and Reset Modes)

The type of data record can be determined by the "Mode byte" in the status portion of the data record, as defined below.  Only Normal and Split type data records should be used to evaluate potential gradient conditions at a mill site.

6.2 Data Record Elements

The data elements that comprise the data record transmitted by the electric field mill are specified below.

6.2.1 Synchronization Pattern (Bytes 1-2)

This fixed pattern (=$D60D) allows the start of the data record to be identified solely on the basis of position in a data stream.  The first character sent to the Base Station will be $D6.

6.2.2 Station Address (Byte 3)

Station Address is used to identify the physical location of the electric field mill.  It can assume values that range from 1 to 64 ($01-$40).  Values out of this range are reserved for future test modes.

6.2.3 Mode/Command Byte (Byte 4)

The less significant nibble of this byte identifies the current mode of operation of the mill.  The more significant nibble of the byte functions as a command echo and indicates the last command received from the base station.

6.2.3.1 Mode Nibble

The specifications for the Mode portion of the Mode/Command Byte are:

[xxxx 0001] Normal Mode

[xxxx 0010] Split Mode

[xxxx 0011] Calibration Mode

[xxxx 0100] Self-Test mode

[xxxx 0101] Reset mode

[xxxx 0111] CRC Transmission Error

[xxxx 1000 - xxxx 1110] Undefined

[xxxx 1111] Sensor Inoperative

where  '[xxxx xxxx]' implies an 8 bit binary bit pattern ('x' implies "don't care" for that bit position).

CRC Transmission Error and Sensor Inoperative are not true mill operating modes, but are provided to allow the Base Station a means of flagging an error condition.

CRC Transmission Error is a flagging state that is set by the base station computer when corruption of a data record by the communication medium is detected at the base station computer via a CRC mismatch. The base station computer overwrites whatever mode pattern was received in the data record.  The Station Address should also be re-written in the data record by the base station computer to guarantee correlation of transmission errors with the correct mill site by users of the electric field mill data records.

Sensor Inoperative is a flagging state that is set by the base station computer when a mill site is determined to be non-responsive (non-existent, disconnected, or faulty).  It is assumed that the base station computer will set up a dummy data record with at least a valid Station Address and Mode/Command byte for distribution to users of the electric field mill data records.

6.2.3.2 Command Acknowledgement Nibble

The specifications for the Command Acknowledgement portion of the Mode/Command Byte are:

[0000 xxxx] Normal Mode

[0001 xxxx] Split Mode

[0010 xxxx] Calibration Mode, 0 v/m ref

[0011 xxxx] Calibration Mode, +E1 ref

[0100 xxxx] Calibration Mode, -E1 ref

[0101 xxxx] Calibration Mode, +E2 ref

[0110 xxxx] Calibration Mode, -E2 ref

[0111 xxxx] Self-Test Mode

[1000 xxxx] Reset Mode

[1001 xxxx] Demodulator ref: lock to rotor

[1010 xxxx] Demodulator ref: free of rotor

[1011 xxxx] Motor On

[1100 xxxx] Motor Off

[1101 xxxx - 1111 xxxx] Not defined

6.2.4 Status Bytes (Bytes 5-11)

6.2.4.1 First Status Byte (Byte 5)

Bit 0-1	[xxxx xx00] Imposed field = 0 v/m

[xxxx xx01] Imposed field = + E1 v/m

[xxxx xx10] Imposed field = - E1 v/m

Indicates the commanded state of the imposed calibration electric field (default is zero volts/meter).

Bit 2	[xxxx x0xx] External 110 VAC good

[xxxx x1xx] External 110 VAC fail

Indicates if the supply of external 110 VAC has failed.

Bit 3	[xxxx 0xxx] 110 VAC line protector good

[xxxx 1xxx] 110 VAC line protector fail

Indicates if the 110 VAC transient protector has failed.

Bit 4	[xxx0 xxxx] Potential gradient data valid

[xxx1 xxxx] Potential gradient data not valid

True indicates that:

a)	the Potential gradient data portion of the data record is being used for status reporting in Self-test mode;

b)	the analog-to-digital converter system is not responding;

c)	the mill is in one of the Calibration Modes, or the motor has been commanded off, or the demodulator has been commanded "Free".

Bit 5	[xx0x xxxx] Ref 1 used for calibration field

[xx1x xxxx] Ref 2 used for calibration field

Indicates if the first or second set of calibration reference fields are being utilized in Calibration mode.

Bit 6	[x0xx xxxx] Motor subsystem OK

[x1xx xxxx] Motor subsystem fault

Indicates if the motor system driving the rotor is experiencing a fault.

Bit 7	[0xxx xxxx] NO SYNC

[1xxx xxxx] SYNC

Indicates whether or not the mill's potential gradient sampling and data record transmission timing are synchronized to received Base Station commands.

6.2.4.2 Second Status Byte (Byte 6)

Bit specifications:

Bit 0-5	[xx00 0000 - xx11 1111] Motor velocity

Indicates the current motor velocity (1 RPS/bit)

Bit 6	[x0xx xxxx] Demodulator reference locked

[x1xx xxxx] Demodulator reference free

Indicates if the reference signal used to demodulate the modulated potential gradient signal is locked to the rotor (default) or to an independent, internally generated signal.

Bit 7	[0xxx xxxx] Motor on

[1xxx xxxx] Motor off

Indicates if the motor system has been commanded off (default is on).

6.2.4.3 Third Status Byte (Byte 7)

All 8 bits are used to indicate the current backup battery voltage (0.078 volts/bit).

6.2.4.4 Fourth Status Byte (Byte 8)

The 4 less significant bits act as sub-multiplex identification codes for Status Byte 5 and the 4 more significant bits act as sub-multiplex codes for Status Bytes 6-7.

6.2.4.5 Fifth Status Byte (Byte 9)

This byte can provide up to 16 different indicators depending on the value of the 4 least significant bits of Status Byte 4.  The indicators defined are:

Status Byte 4 Code 	Type	Status Byte 5 Function

[xxxx 0000]						UC	Sensor Head ID (identifies mill head)

[xxxx 0001]						UC	Firmware Version

[xxxx 0010]						UC	Motor Current Monitor (16 mA/bit)

[xxxx 0011]						BC	SCI error log ( 0 -> no err)

Bit 7 = undef

Bit 6 = false TC irq

Bit 5 = undef

Bit 4 = false IDLE irq

Bit 3 = OR err

Bit 2 = NF err

Bit 1 = FE

Bit 0 = UNKNOWN SCI irq

[xxxx 0100]						BC	Bad character rcv'd count

Bits 0-6 = Bad async char cnt (not implemented)

Bit 7 = Bad checksum flag on cmd

[xxxx 0101]						BC	Overflow flags

Bit 0 = RCV_Q overflow

Bit 1 = ADC_Q overflow

Bit 2 = CMD_Q size greater than 1

Bit 3 = Early command

Bit 4 = Illegal command

Bit 5 = Data record overwrite

Bit 6 = ADC timeout flag

Bit 7 = cmd pending flag set w/o cmd          in queue

[xxxx 0110]						BC	MCU Fault flags (not implemented)

Bit 0 = Clock Fail irq occurred

Bit 1 = COP Watchdog timeout irq             occurred

Bit 2 = Illegal Op Code Trap irq             occurred

Bit 3 = XIRQ occurred

Bits 4-7 = undef

[xxxx 0111]						UC	BUF_SKIPPED count = # "START_XMT_SEQ" skips (not implemented)

Status Byte 4 Code 	Type	Status Byte 5 Function

[xxxx 1000]						UC	BAD_FILL_CNT: cnts each occurence of illegal "BUF_FILL_P"

[xxxx 1001]						UC	CONFIG_REG: reports value of 68HC11 configuration register programmed into internal EEPROM. (Should be = 09h to enable 'HC11 Computer Operating Properly Watchdog function).

[xxxx 1010-xxxx 1111]	X		Spare

6.2.4.6 Sixth and Seventh Status Bytes (Bytes 10-11)

These bytes can provide up to 16 different indicators depending on the value of the 4 most significant bits of Status Byte 4.  The indicators defined are:

Status Byte 4 Code 	Type	Status Bytes 6 & 7 Function

[0000 xxxx]					I			Rotor (Cal) Voltage (6.04 mV/bit)

[0001 xxxx]					UI		Motor Fault Pulse Count

[0010 xxxx]					UI		Idle Loop Count

[0011 xxxx]					UI		LOCK_2_FREE count = # occurrences of LOCK to FREE sync mode

[0100 xxxx]					UI		FREE_2_LOCK count = # occurrences of FREE to LOCK sync mode

[0101 xxxx]					UI		REC_OVRW_CNT count = # occurrences of data rec overwrite

[0110 xxxx]					UI		Max interval between arrival of Base Stn cmds

[0111 xxxx]					UI		Min interval between arrival of Base Stn cmds

[1000 xxxx-

1111 xxxx]				X			Spare

6.2.5 Raingauge (Byte 12)

The Raingauge tip count indicates the number of tips detected during the last second.

6.2.6 Potential Gradient Data or Extended Status Report

(Bytes 13-112)

Depending on the mode of operation, the 100 bytes associated with this section of the data record will contain digitized potential gradient samples, digitized external signal samples, or an extended status report (see section 5.1).

6.2.6.1 Potential gradient Data

The three types of data records that contain potential gradient data are Normal, Split, and Calibration.  See section 5.1 for a description of each.  The 50 potential gradient samples are in the form of two's complement 16 bit integers in Motorola byte order, with one LSB corresponding to 4 volts/meter.

6.2.6.2 Extended Status

The following bytes are defined as the extended status indicators for the Reset and Sensor Self-Test modes, with

a) a zero value ($00) indicating that the test was not executed;

b) a value = 1 ($01) indicating that the test was successful

c) a value = -1 ($FF) indicating that the test failed

Byte 13:	Microprocessor EPROM checksum test

Byte 14:	MC68HC11 internal RAM test

Byte 15:	Microprocessor external SRAM test

Byte 16:	Microprocessor internal Serial Communications Interface test

Byte 17:	R65C22 Versatile Interface Adapter test

Byte 18:	Microprocessor internal intervalometer test

Bytes 19-112: Undefined

(Note:	Extended status is not implemented for

firmware ver 5 = MSFCEFM5)

6.2.7 CRC-16 Value (Bytes 113-114)

This parameter is a 16-bit cyclic redundancy check value computed over all bytes (1-112) of the data record by the mill microprocessor using the CRC-16 generator polynomial.

7 Potential Communication Error Sources and Solutions

Since the data communication link may consist of very long (to 25 miles) wire pairs which may be routed through multiplexers, the following deviations from ideal conditions can be expected to occur:

1.	A propagation delay will exist for each link that will exhibit a fixed delay and a variable delay (jitter) due to mutiplexer proceesing delays;

2.	Noise and interference due to lightning activity or anthropomorphic noise sources can couple into the communications channel.

The design of the communications protocol between the mills and the base station should allow correct operation of the network while these conditions exist.